## Freq of failure
Wind Farm | Frequency of failure
15 | 246
2 | 173
14 | 138
1 | 57
11 | 54
4 | 44
6 | 28
5 | 27
9 | 18
8 | 6
7 | 4
16 | 4
13 | 4
12 | 3
10 | 2
3 | 1
Grand Total | 809

## Component problems
Wind turbine manufacturer | Frequency of component problems
1 | 15
2 | 33
3 | 14
4 | 6
5 | 40
Grand Total | 108

## Sheet3
Sum of Wind Turbine | Wind Turbine
Technology | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 22 | 24 | Grand Total
Blade bearing | 2 | [21 empty] | 2
Blade bearings | 2 | 4 | 3 | 8 | 5 | 6 | 14 | 8 | 9 | 10 | 22 | 24 | 13 | 14 | 30 | 32 | 17 | 36 |  | 20 |  | 24 | 301
Blade repairs |  | 2 |  |  |  | 6 | [16 empty] | 8
Gearbox | 3 | 2 | 9 | 20 | 10 | 24 | 7 | 24 |  |  | 11 | 12 | 13 | 14 |  | 16 |  |  | 19 |  |  |  | 184
Generator | [12 empty] | 13 | 14 |  | 16 | [6 empty] | 43
Generator main circuit breaker | [8 empty] | 9 | [13 empty] | 9
Main bearing |  |  |  | 4 | [18 empty] | 4
Main inverter |  | 2 |  |  | 5 | 6 | [16 empty] | 13
Rear bearing |  |  |  | 4 | [18 empty] | 4
Rotor bolts | [20 empty] | 22 | 24 | 46
Switchgear | [6 empty] | 7 |  |  | 10 | [12 empty] | 17
Transformer | 6 | 10 | 9 | 20 |  | 6 | 14 | 8 |  | 20 | 11 |  | 13 |  | 15 | 16 | 17 | [5 empty] | 165
Yaw bearing | 1 | [21 empty] | 1
Yaw gears | 2 | [8 empty] | 10 | [12 empty] | 12
Grand Total | 16 | 20 | 21 | 56 | 20 | 48 | 42 | 40 | 18 | 50 | 44 | 36 | 52 | 42 | 45 | 80 | 34 | 36 | 19 | 20 | 22 | 48 | 809

## Sheet4
| Wind Turbine | [23 empty] | Importance
Technology | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 22 | 24 | Grand Total | Year | High | Low | Medium | Grand Total
Blade bearing | 2 | [21 empty] | 2 | Blade bearing |  |  | 2 | 2
Blade bearings | 2 | 4 | 3 | 8 | 5 | 6 | 14 | 8 | 9 | 10 | 22 | 24 | 13 | 14 | 30 | 32 | 17 | 36 |  | 20 |  | 24 | 301 | Blade bearings |  |  | 29 | 29
Blade repairs |  | 2 |  |  |  | 6 | [16 empty] | 8 | Blade repairs |  |  | 2 | 2
Gearbox | 3 | 2 | 9 | 20 | 10 | 24 | 7 | 24 |  |  | 11 | 12 | 13 | 14 |  | 16 |  |  | 19 |  |  |  | 184 | Gearbox | 28 |  |  | 28
Generator | [12 empty] | 13 | 14 |  | 16 | [6 empty] | 43 | Generator | 3 |  |  | 3
Generator main circuit breaker | [8 empty] | 9 | [13 empty] | 9 | Generator main circuit breaker |  | 1 |  | 1
Main bearing |  |  |  | 4 | [18 empty] | 4 | Main bearing |  |  | 1 | 1
Main inverter |  | 2 |  |  | 5 | 6 | [16 empty] | 13 | Main inverter |  |  | 3 | 3
Rear bearing |  |  |  | 4 | [18 empty] | 4 | Rear bearing |  |  | 1 | 1
Rotor bolts | [20 empty] | 22 | 24 | 46 | Rotor bolts | 2 |  |  | 2
Switchgear | [6 empty] | 7 |  |  | 10 | [12 empty] | 17 | Switchgear |  |  | 2 | 2
Transformer | 6 | 10 | 9 | 20 |  | 6 | 14 | 8 |  | 20 | 11 |  | 13 |  | 15 | 16 | 17 | [5 empty] | 165 | Transformer | 30 |  |  | 30
Yaw bearing | 1 | [21 empty] | 1 | Yaw bearing |  | 1 |  | 1
Yaw gears | 2 | [8 empty] | 10 | [12 empty] | 12 | Yaw gears |  | 3 |  | 3
Grand Total | 16 | 20 | 21 | 56 | 20 | 48 | 42 | 40 | 18 | 50 | 44 | 36 | 52 | 42 | 45 | 80 | 34 | 36 | 19 | 20 | 22 | 48 | 809

## Sheet5
Count of Importance | Importance
Year | High | Low | Medium | Grand Total
Blade bearing |  |  | 2 | 2
Blade bearings |  |  | 29 | 29
Blade repairs |  |  | 2 | 2
Gearbox | 28 |  |  | 28
Generator | 3 |  |  | 3
Generator main circuit breaker |  | 1 |  | 1
Main bearing |  |  | 1 | 1
Main inverter |  |  | 3 | 3
Rear bearing |  |  | 1 | 1
Rotor bolts | 2 |  |  | 2
Switchgear |  |  | 2 | 2
Transformer | 30 |  |  | 30
Yaw bearing |  | 1 |  | 1
Yaw gears |  | 3 |  | 3
Grand Total | 63 | 5 | 40 | 108

## Faults
Wind farm | Wind Turbine | Year | Wind turbine manufacturer | Component name | Importance
1 | 8 | 2008 | 1 | Gearbox | High
1 | 4 | 2009 | 1 | Gearbox | High
1 | 6 | 2009 | 1 | Gearbox | High
1 | F | 2011 | 1 | Gearbox | High
1 | 2 | 2011 | 1 | Gearbox | High
1 | 2 | 2011 | 1 | Main inverter | Medium
1 | 5 | 2011 | 1 | Main inverter | Medium
1 | 6 | 2011 | 1 | Main inverter | Medium
2 | 4 | 2012 | 2 | Transformer | High
3 | 1 | 2012 | 3 | Transformer | High
4 | 17 | 2012 | 3 | Transformer | High
1 | 3 | 2012 | 1 | Gearbox | High
5 | 2 | 2013 | 2 | Transformer | High
6 | 8 | 2013 | 2 | Gearbox | High
7 | 4 | 2013 | 3 | Transformer | High
8 | 1 | 2013 | 3 | Transformer | High
8 | 3 | 2013 | 3 | Transformer | High
4 | 10 | 2013 | 3 | Yaw gears | Low
9 | 4 | 2013 | 4 | Gearbox | High
5 | 3 | 2014 | 2 | Gearbox | High
2 | 11 | 2014 | 2 | Gearbox | High
2 | 16 | 2014 | 2 | Gearbox | High
10 | 1 | 2014 | 3 | Transformer | High
11 | 9 | 2014 | 5 | Blade bearings | Medium
5 | 4 | 2015 | 2 | Gearbox | High
2 | 8 | 2015 | 2 | Transformer | High
2 | 10 | 2015 | 2 | Transformer | High
2 | 7 | 2015 | 2 | Gearbox | High
12 | 1 | 2015 | 2 | Transformer | High
12 | 2 | 2015 | 2 | Transformer | High
6 | 6 | 2015 | 2 | Gearbox | High
10 | 1 | 2015 | 3 | Yaw gears | Low
4 | 10 | 2015 | 3 | Switchgear | Medium
13 | 3 | 2015 | 3 | Transformer | High
11 | 5 | 2015 | 5 | Blade bearings | Medium
11 | 6 | 2015 | 5 | Blade bearings | Medium
11 | 7 | 2015 | 5 | Blade bearings | Medium
11 | 8 | 2015 | 5 | Blade bearings | Medium
14 | 11 | 2015 | 5 | Blade bearings | Medium
14 | 12 | 2015 | 5 | Blade bearings | Medium
14 | 13 | 2015 | 5 | Blade bearings | Medium
14 | 15 | 2015 | 5 | Blade bearings | Medium
14 | 17 | 2015 | 5 | Blade bearings | Medium
14 | 18 | 2015 | 5 | Blade bearings | Medium
1 | 1 | 2015 | 1 | Gearbox | High
5 | 4 | 2016 | 2 | Transformer | High
2 | 16 | 2016 | 2 | Transformer | High
2 | 6 | 2016 | 2 | Gearbox | High
2 | 14 | 2016 | 2 | Gearbox | High
11 | 1 | 2016 | 5 | Blade bearings | Medium
11 | 2 | 2016 | 5 | Blade bearings | Medium
11 | 3 | 2016 | 5 | Blade bearings | Medium
11 | 4 | 2016 | 5 | Blade bearings | Medium
11 | 9 | 2016 | 5 | Generator main circuit breaker | Low
14 | 10 | 2016 | 5 | Blade bearings | Medium
14 | 14 | 2016 | 5 | Blade bearings | Medium
14 | 16 | 2016 | 5 | Blade bearings | Medium
9 | 1 | 2016 | 4 | Gearbox | High
4 | 7 | 2017 | 3 | Switchgear | Medium
14 | 12 | 2017 | 5 | Blade bearings | Medium
15 | 19 | 2017 | 5 | Gearbox | High
1 | 2 | 2017 | 1 | Transformer | High
1 | 4 | 2017 | 1 | Transformer | High
9 | 1 | 2017 | 4 | Yaw gears | Low
9 | 2 | 2017 | 4 | Blade repairs | Medium
9 | 6 | 2017 | 4 | Blade repairs | Medium
2 | 1 | 2018 | 2 | Transformer | High
2 | 3 | 2018 | 2 | Transformer | High
2 | 10 | 2018 | 2 | Transformer | High
2 | 11 | 2018 | 2 | Transformer | High
2 | 15 | 2018 | 2 | Transformer | High
6 | 6 | 2018 | 2 | Gearbox | High
6 | 8 | 2018 | 2 | Gearbox | High
15 | 2 | 2018 | 5 | Blade bearings | Medium
15 | 24 | 2018 | 5 | Blade bearings | Medium
15 | 15 | 2018 | 5 | Blade bearings | Medium
15 | 7 | 2018 | 5 | Blade bearings | Medium
1 | 4 | 2018 | 1 | Gearbox | High
1 | 2 | 2018 | 1 | Transformer | High
5 | 5 | 2019 | 2 | Gearbox | High
2 | 1 | 2019 | 2 | Transformer | High
2 | 4 | 2019 | 2 | Transformer | High
5 | 2 | 2019 | 2 | Transformer | High
8 | 1 | 2019 | 3 | Yaw bearing | Low
8 | 1 | 2019 | 3 | Blade bearing | Medium
13 | 1 | 2019 | 3 | Blade bearing | Medium
15 | 1 | 2019 | 5 | Blade bearings | Medium
15 | 11 | 2019 | 5 | Blade bearings | Medium
15 | 4 | 2019 | 5 | Blade bearings | Medium
15 | 20 | 2019 | 5 | Blade bearings | Medium
15 | 16 | 2019 | 5 | Blade bearings | Medium
15 | 18 | 2019 | 5 | Blade bearings | Medium
5 | 7 | 2020 | 2 | Transformer | High
2 | 13 | 2020 | 2 | Transformer | High
2 | 6 | 2020 | 2 | Transformer | High
15 | 14 | 2020 | 5 | Generator | High
15 | 4 | 2020 | 5 | Gearbox | High
1 | 7 | 2020 | 1 | Transformer | High
15 | 3 | 2021 | 5 | Gearbox | High
15 | 24 | 2021 | 5 | Rotor bolts | High
15 | 22 | 2021 | 5 | Rotor bolts | High
15 | 13 | 2021 | 5 | Generator | High
15 | 13 | 2021 | 5 | Gearbox | High
15 | 16 | 2021 | 5 | Generator | High
16 | 4 | 2021 | 5 | Rear bearing | Medium
9 | 4 | 2021 | 4 | Main bearing | Medium
2 | 5 | 2021 | 2 | Gearbox | High
2 | 12 | 2021 | 2 | Gearbox | High